## NDPL
DELHI TRANSCO LIMITED | [15 empty] | MARCH-2011
REACTIVE ENERGY CONSUMPTION STATEMENT
Customer:NORTH DELHI POWER LIMITED.
NDPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
GOPAL PUR
1 | Tx.1 | 4864904 | ELSTER | Kvarh(Lead/Lag) | -1000 | 19000 | 19676 | -676 | 676000 | 0.676 | 979262 | 979264 | -2 | 2000 | 0.002
2 | Tx.2 | 4902499 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999265 | 999484 | -219 | 219000 | 0.219 | 992857 | 994087 | -1230 | 1230000 | 1.23 | ROLL OVER
3 | Tx.3 | 4864905 | ELSTER | Kvarh(Lead/Lag) | -1000 | 20714 | 21083 | -369 | 369000 | 0.369 | 1259 | 1261 | -2 | 2000 | 0.002
SUBZI MANDI
4 | Tx.1 | 4864912 | ELSTER | Kvarh(Lead/Lag) | -1000 | 975058 | 974897 | 161 | -161000 | -0.161 | 987887 | 988202 | -315 | 315000 | 0.315
5 | Tx.2 | 4864913 | ELSTER | Kvarh(Lead/Lag) | -1000 | 923583 | 923854 | -271 | 271000 | 0.271 | 960164 | 960712 | -548 | 548000 | 0.548
ROHINI
6 | Tx.1 | 4864982 | ELSTER | Kvarh(Lead/Lag) | -1000 | 18182 | 17885 | 297 | -297000 | -0.297 | 12430 | 11878 | 552 | -552000 | -0.552
7 | Tx.2 | 4864983 | ELSTER | Kvarh(Lead/Lag) | -1000 | 19188 | 18873 | 315 | -315000 | -0.315 | 9132 | 8659 | 473 | -473000 | -0.473
8 | Tx.-3 | 4864953 | ELSTER | Kvarh(Lead/Lag) | -1000 | 17119 | 17063 | 56 | -56000 | -0.056 | 997186 | 997016 | 170 | -170000 | -0.17
9 | Tx.-4 | 4864984 | ELSTER | Kvarh(Lead/Lag) | -1000 | 11980 | 11966 | 14 | -14000 | -0.014 | 988459 | 988529 | -70 | 70000 | 0.07
SHALIMAR BAGH
10 | Tx.1 | 4864939 | ELSTER | Kvarh(Lead/Lag) | -1000 | 35824 | 36106 | -282 | 282000 | 0.282 | 9908 | 9936 | -28 | 28000 | 0.028
11 | Tx.-2 | 4864940 | ELSTER | Kvarh(Lead/Lag) | -1000 | 3394 | 3867 | -473 | 473000 | 0.473 | 4235 | 4237 | -2 | 2000 | 0.002
12 | Tx.-3 | 5128410 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999089 | 999404 | -315 | 315000 | 0.315 | 999963 | 999975 | -12 | 12000 | 0.012
13 | 220KV DMRC | 4865060 | ELSTER | Kvarh(Lead/Lag) | 1000 | 968733 | 970519 | -1786 | -1786000 | -1.786 | 920612 | 920612 | 0 | 0 | 0
NARELA
14 | Tx.1 | 4865034 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997491 | 997517 | -26 | 26000 | 0.026 | 16316 | 16030 | 286 | -286000 | -0.286
15 | Tx.2 | 4865035 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998366 | 998253 | 113 | -113000 | -0.113 | 18437 | 18428 | 9 | -9000 | -0.009
16 | Tx.3 | 4902500 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1102 | 1021 | 81 | -81000 | -0.081 | 20905 | 20572 | 333 | -333000 | -0.333
NARAINA
17 | O/G REWARI LINE 1 | 4864886 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999622 | 999684 | -62 | -62000 | -0.062 | 31417 | 31346 | 71 | 71000 | 0.071
18 | O/G REWARI LINE 2 | 4864887 | ELSTER | Kvarh(Lead/Lag) | 1000 | 156 | 163 | -7 | -7000 | -0.007 | 25995 | 25918 | 77 | 77000 | 0.077
19 | 16 MVA TX.-1 | 4864798 | ELSTER | Kvarh(Lead/Lag) | 100 | 1722 | 1694 | 28 | 2800 | 0.0028 | 100146 | 98954 | 1192 | 119200 | 0.1192
20 | 16 MVA TX.-2 | 4864799 | ELSTER | Kvarh(Lead/Lag) | 100 | 2720 | 2460 | 260 | 26000 | 0.026 | 155929 | 154626 | 1303 | 130300 | 0.1303
21 | INDER PURI | 4864888 | ELSTER | Kvarh(Lead/Lag) | 1000 | 996101 | 996239 | -138 | -138000 | -0.138 | 998360 | 998425 | -65 | -65000 | -0.065
22 | INDER PURI-2 | 5128402 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999933 | 1000008 | -75 | -75000 | -0.075 | 999972 | 1000060 | -88 | -88000 | -0.088
KASHMIRI GATE
23 | 221 kV DMRC #1 | 4865057 | ELSTER | Kvarh(Lead/Lag) | 1000 | 655317 | 655682 | -365 | -365000 | -0.365 | 803250 | 803363 | -113 | -113000 | -0.113
24 | 221 kV DMRC #2 | 4865058 | ELSTER | Kvarh(Lead/Lag) | 1000 | 662597 | 662932 | -335 | -335000 | -0.335 | 834741 | 834763 | -22 | -22000 | -0.022
25 | CIVIL LINE | 4864889 | ELSTER | Kvarh(Lead/Lag) | 1000 | 992446 | 992474 | -28 | -28000 | -0.028 | 998661 | 998659 | 2 | 2000 | 0.002
26 | CIVIL LINE-2 | 4864800 | ELSTER | Kvarh(Lead/Lag) | 100 | 993740 | 993559 | 181 | 18100 | 0.0181 | 12386 | 12137 | 249 | 24900 | 0.0249 | FINAL READING 28/3/11 DUE TO FAULTY METER
KANJAWALA
27 | TX-1 | 4865054 | ELSTER | Kvarh(Lead/Lag) | -1000 | 6301 | 6019 | 282 | -282000 | -0.282 | 981704 | 981589 | 115 | -115000 | -0.115
28 | Tx.2 | 4865055 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996578 | 996686 | -108 | 108000 | 0.108 | 949646 | 949977 | -331 | 331000 | 0.331
BAWANA
29 | I/C 100 MVA PR.TR. | 4865056 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993067 | 993326 | -259 | 259000 | 0.259 | 952637 | 954224 | -1587 | 1587000 | 1.587
EXPORT TO EAST & CENTRE
IMPORTS
SHASTRI PARK
30 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | 1000 | 529 | 520 | 9 | 9000 | 0.009 | 14199 | 13790 | 409 | 409000 | 0.409
31 | PUSA GRID-II | 4864844 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998887 | 998887 | 0 | 0 | 0 | 3516 | 3333 | 183 | 183000 | 0.183
| NDPL(+) continue | [14 empty] | MARCH-2011
DMS
32 | 33KV PANDAV NGR | 4865169 | ELSTER | Kvarh(Lead/Lag) | 1000 | 607 | 473 | 134 | 134000 | 0.134 | 51056 | 50767 | 289 | 289000 | 0.289
REWARI LINE
33 | 20MVA Tx-2 | 4864824 | ELSTER | Kvarh(Lead/Lag) | 100 | 9192 | 8898 | 294 | 29400 | 0.0294 | 44885 | 44377 | 508 | 50800 | 0.0508
VISHAL
34 | RAMESH NAGAR-1 | 4865090 | ELSTER | Kvarh(Lead/Lag) | 100 | 6231 | 6042 | 189 | 18900 | 0.0189 | 8141 | 7171 | 970 | 97000 | 0.097
35 | BALI NAGAR -1 | 4902519 | ELSTER | Kvarh(Lead/Lag) | 100 | 8264 | 8245 | 19 | 1900 | 0.0019 | 26496 | 25662 | 834 | 83400 | 0.0834
36 | ESI HOSPITAL | 4902520 | ELSTER | Kvarh(Lead/Lag) | 100 | 13706 | 13613 | 93 | 9300 | 0.0093 | 35231 | 34647 | 584 | 58400 | 0.0584
S.B.MILL
37 | MOTI NAGAR KIOSK | 4902521 | ELSTER | Kvarh(Lead/Lag) | 100 | 28912 | 28353 | 559 | 55900 | 0.0559 | 8523 | 8523 | 0 | 0 | 0
38 | 53 RAMA ROAD | 4902522 | ELSTER | Kvarh(Lead/Lag) | 100 | 840 | 840 | 0 | 0 | 0 | 185 | 185 | 0 | 0 | 0
39 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | 100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
40 | 70 RAMA ROAD | 4902524 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | MOTI NAGAR 2 | 4902525 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | NAJAFGARH ROAD | 4902526 | ELSTER | Kvarh(Lead/Lag) | 100 | 13825 | 13371 | 454 | 45400 | 0.0454 | 8414 | 8346 | 68 | 6800 | 0.0068
43 | PHILIPS | 4902527 | ELSTER | Kvarh(Lead/Lag) | 100 | 997829 | 997815 | 14 | 1400 | 0.0014 | 999975 | 999975 | 0 | 0 | 0
B.G.ROAD
44 | CSA | 4902529 | ELSTER | Kvarh(Lead/Lag) | 500 | 3437 | 3421 | 16 | 8000 | 0.008 | 26459 | 26218 | 241 | 120500 | 0.1205
45 | DCM NO.1 | 4902530 | ELSTER | Kvarh(Lead/Lag) | 500 | 3183 | 3166 | 17 | 8500 | 0.0085 | 18011 | 17829 | 182 | 91000 | 0.091
46 | DCM NO.2 | 4902531 | ELSTER | Kvarh(Lead/Lag) | 500 | 3225 | 3208 | 17 | 8500 | 0.0085 | 12176 | 12059 | 117 | 58500 | 0.0585
47 | SADAR S/S | 4902532 | ELSTER | Kvarh(Lead/Lag) | 500 | 3179 | 3165 | 14 | 7000 | 0.007 | 13881 | 13741 | 140 | 70000 | 0.07
D.M.S.
48 | PHILIPS | 4902535 | ELSTER | Kvarh(Lead/Lag) | 100 | 999533 | 999562 | -29 | -2900 | -0.0029 | 4740 | 4724 | 16 | 1600 | 0.0016
49 | 69 NG ROAD | 4902536 | ELSTER | Kvarh(Lead/Lag) | 100 | 2046 | 1817 | 229 | 22900 | 0.0229 | 11593 | 11518 | 75 | 7500 | 0.0075
50 | J BLOCK KIRTI NGR | 4902537 | ELSTER | Kvarh(Lead/Lag) | 100 | 4694 | 4343 | 351 | 35100 | 0.0351 | 44307 | 44121 | 186 | 18600 | 0.0186
51 | H BLOCK | 4902538 | ELSTER | Kvarh(Lead/Lag) | 100 | 8211 | 8079 | 132 | 13200 | 0.0132 | 19022 | 19016 | 6 | 600 | 0.0006
52 | SHADI KHAM PUR | 4902539 | ELSTER | Kvarh(Lead/Lag) | 100 | 999751 | 999783 | -32 | -3200 | -0.0032 | 282 | 283 | -1 | -100 | -0.0001
53 | BREAK FAST | 4902540 | ELSTER | Kvarh(Lead/Lag) | 100 | 15 | 15 | 0 | 0 | 0 | 13398 | 13398 | 0 | 0 | 0
FAIZ ROAD
54 | TIBIA COLLEGE-1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | 100 | 963 | 926 | 37 | 3700 | 0.0037 | 55073 | 54452 | 621 | 62100 | 0.0621
55 | TIBIA COLLEGE-2 | 4902542 | ELSTER | Kvarh(Lead/Lag) | 100 | 673 | 599 | 74 | 7400 | 0.0074 | 49801 | 49491 | 310 | 31000 | 0.031
56 | MANAK PURA | 4902543 | ELSTER | Kvarh(Lead/Lag) | 100 | 898 | 796 | 102 | 10200 | 0.0102 | 71613 | 71027 | 586 | 58600 | 0.0586
KASHMIRI GATE
57 | 20MVA TX. | 4864807 | ELSTER | Kvarh(Lead/Lag) | 100 | 85941 | 84600 | 1341 | 134100 | 0.1341 | 25947 | 25729 | 218 | 21800 | 0.0218
58 | FLYOVER | 4865086 | ELSTER | Kvarh(Lead/Lag) | 100 | 8118 | 7947 | 171 | 17100 | 0.0171 | 28896 | 28045 | 851 | 85100 | 0.0851
59 | B/C (IMP. TO NDPL) | 4902571 | ELSTER | Kvarh(Lead/Lag) | -300 | 2 | 2 | 0 | 0 | 0 | 999951 | 999944 | 7 | -2100 | -0.0021
REWARI LINE (11KV TRANSFER OF ENERGY)
60 | BSES -NDPL(EX.) ON BUS-1&2 | 4902514 | ELSTER | Kvarh(Lead/Lag) | -100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | METER FAULTY
60 | BSES -NDPL(EX.) ON BUS-1&2 | 4865087 | ELSTER | Kvarh(Lead/Lag) | -400 | 4567 | 4567 | 0 | 0 | 0 | 12600 | 12592 | 8 | -3200 | -0.0032 | INSTALLED ON 23/03/11 AGAINST DEFECTIVE MTR. 4902514
61 | BSES -NDPL(EX.) ON BUS-2&3 | 4902516 | ELSTER | Kvarh(Lead/Lag) | 100 | 999377 | 999472 | -95 | -9500 | -0.0095 | 999145 | 999160 | -15 | -1500 | -0.0015
| ENERGY INPUT AT 66/33/11 KV LEVEL | [8 empty] | -0.5048 |  |  |  |  | 4.1228
NDPL(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 % |  |  | MARCH-2011
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
NARAINA
1 | GOPI NATH BAZAAR | 4865092 | ELSTER | Kvarh(Lead/Lag) | -100 | 4214 | 4111 | 103 | -10300 | -0.0103 | 7583 | 7556 | 27 | -2700 | -0.0027
MANGOLPURI
2 | NANGLOI-1 EXP | 4864954 | ELSTER | Kvarh(Lead/Lag) | -1000 | 4330 | 4331 | -1 | 1000 | 0.001 | 3697 | 3687 | 10 | -10000 | -0.01
3 | NANGLOI-2 EXP | 4864955 | ELSTER | Kvarh(Lead/Lag) | -1000 | 5745 | 5741 | 4 | -4000 | -0.004 | 3919 | 3914 | 5 | -5000 | -0.005
SUBZI MANDI
4 | O/G BG Rd.1 | 4864808 | ELSTER | Kvarh(Lead/Lag) | -200 | 3536 | 3562 | -26 | 5200 | 0.0052 | 3141 | 3241 | -100 | 20000 | 0.02
5 | O/G BG Rd.2 | 4864841 | ELSTER | Kvarh(Lead/Lag) | -1000 | 12742 | 12536 | 206 | -206000 | -0.206 | 11231 | 10523 | 708 | -708000 | -0.708
SUDARSHAN PARK
6 | VISHAL (EXP) | 4864792 | ELSTER | Kvarh(Lead/Lag) | -100 | 36227 | 34534 | 1693 | -169300 | -0.1693 | 146577 | 147860 | -1283 | 128300 | 0.1283
REWARI LINE (ENERGY EXCHANGE WITH NDPL)
7 | 33KV B/C | 4865170 | ELSTER | Kvarh(Lead/Lag) | -1000 | 0 | 0 | 0 | 0 | 0 | 999975 | 999975 | 0 | 0 | 0
KANJAWALA
8 | 66KV DMRC | 4864961 | ELSTER | Kvarh(Lead/Lag) | -1000 | 983068 | 983494 | -426 | 426000 | 0.426 | 993320 | 993647 | -327 | 327000 | 0.327
66KV GHEBRA
9 | GHEBRA-NANGLOI | 4902502 | ELSTER | Kvarh(Lead/Lag) | -1250 | 998227 | 998396 | -169 | 211250 | 0.21125 | 999974 | 999841 | 133 | -166250 | -0.16625 | LOADED ON 04/03/2011
| TOTAL OF INTER COMPANY EXCHANGE POINTS | [8 empty] | 0.25385 |  |  |  |  | -0.41665
EXECUTIVE SUMMERY N.D.P.L.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (Refer sheet NDPL(+)) | [9 empty] | -0.5048 |  |  |  |  | 4.1228
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet NDPL(-)) | [9 empty] | 0.25385 |  |  |  |  | -0.41665
3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL) | [9 empty] | 1.6576 |  |  |  |  | 0.054038
NET ENERGY TO NORTH DELHI POWER LIMITED | [9 empty] | 1.4067 |  |  |  |  | 3.7602
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 1.4067 | (REACTIVE MUs) |  |  |  | 3.7602 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.1873 | (REACTIVE MUs) |  |  |  | 0.35271 | (REACTIVE MUs)
ASSESSMENT OF BYPL FEEDERS AT GAS TURBINE DMRC-I,DMRC-II,AKSHARDHAM FOR THE PERIOD ( OCT.2010 TO JAN.2011) | [9 empty] | 0.42003 |  |  |  |  | 9.9633
[9 empty] | TOTAL | 1.6394 | (REACTIVE MUs) |  |  |  | 14.0762 | (REACTIVE MUs)

## BYPL
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [15 empty] | MARCH-2011
Customer:BSES YAMUNA POWER LIMITED.
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION 33KV FEEDER
1 | KAMLA MKT.-B-18 | 4865098 | ELSTER | Kvarh(Lead/Lag) | 100 | 999998 | 999998 | 0 | 0 | 0 | 37954 | 37954 | 0 | 0 | 0
2 | KAMLA MKT.B-30 | 4865161 | ELSTER | Kvarh(Lead/Lag) | 100 | 995030 | 995668 | -638 | -63800 | -0.0638 | 72118 | 71485 | 633 | 63300 | 0.0633
3 | P. HOSPITAL BAY-19 | 4865099 | ELSTER | Kvarh(Lead/Lag) | 100 | 14322 | 14887 | -565 | -56500 | -0.0565 | 996606 | 997172 | -566 | -56600 | -0.0566
4 | IG STD- BAY-29 | 4865162 | ELSTER | Kvarh(Lead/Lag) | 100 | 22046 | 22229 | -183 | -18300 | -0.0183 | 29357 | 29018 | 339 | 33900 | 0.0339
5 | IG STD-BAY 31 | 4865100 | ELSTER | Kvarh(Lead/Lag) | 100 | 998890 | 999058 | -168 | -16800 | -0.0168 | 999475 | 998181 | 1294 | 129400 | 0.1294
6 | DELHI GATE B-17 | 4865101 | ELSTER | Kvarh(Lead/Lag) | 100 | 8880 | 8683 | 197 | 19700 | 0.0197 | 69570 | 68177 | 1393 | 139300 | 0.1393
7 | MINTO RD. B-34 | 4865102 | ELSTER | Kvarh(Lead/Lag) | 100 | 1000081 | 999248 | 833 | 83300 | 0.0833 | 47610 | 46722 | 888 | 88800 | 0.0888 | ROLL OVER
RPH
8 | KAMLA MKT.-2 | 4864884 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999984 | 999987 | -3 | -3000 | -0.003 | 214 | 209 | 5 | 5000 | 0.005
9 | FOUNTAIN BAY-16 | 4864831 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999907 | 999912 | -5 | -5000 | -0.005 | 2296 | 2278 | 18 | 18000 | 0.018
10 | MINTO RD BAY-17 | 4864832 | ELSTER | Kvarh(Lead/Lag) | 1000 | 104 | 101 | 3 | 3000 | 0.003 | 1431 | 1423 | 8 | 8000 | 0.008
11 | TOWN HALL-3 | 4864833 | ELSTER | Kvarh(Lead/Lag) | 1000 | 156 | 188 | -32 | -32000 | -0.032 | 2630 | 2638 | -8 | -8000 | -0.008
12 | LAHORI GATE-1 | 4864834 | ELSTER | Kvarh(Lead/Lag) | 1000 | 205 | 213 | -8 | -8000 | -0.008 | 1745 | 1844 | -99 | -99000 | -0.099
13 | LAHORI GATE-2 | 4864835 | ELSTER | Kvarh(Lead/Lag) | 1000 | 319 | 312 | 7 | 7000 | 0.007 | 1358 | 765 | 593 | 593000 | 0.593
14 | JAMA MASJID-1 | 4864836 | ELSTER | Kvarh(Lead/Lag) | 1000 | 32 | 31 | 1 | 1000 | 0.001 | 13503 | 13331 | 172 | 172000 | 0.172
15 | JAMA MASJID-2 | 4864837 | ELSTER | Kvarh(Lead/Lag) | 1000 | 153 | 136 | 17 | 17000 | 0.017 | 33649 | 33548 | 101 | 101000 | 0.101
16 | GB PANTH(Bay-13) | 4864838 | ELSTER | Kvarh(Lead/Lag) | 1000 | 261 | 261 | 0 | 0 | 0 | 8184 | 7175 | 1009 | 1009000 | 1.009
17 | SACHV. (Bay-12) | 4864839 | ELSTER | Kvarh(Lead/Lag) | 1000 | 194 | 229 | -35 | -35000 | -0.035 | 5040 | 5055 | -15 | -15000 | -0.015
18 | 6.6 KV IRRG.PUMP | 4864786 | ELSTER | Kvarh(Lead/Lag) | 100 | 28711 | 28663 | 48 | 4800 | 0.0048 | 418 | 418 | 0 | 0 | 0
19 | KAMLA MKT. (B-19) | 4864883 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998958 | 998954 | 4 | 4000 | 0.004 | 5029 | 5011 | 18 | 18000 | 0.018
GT
20 | DMRC. CKT.-I | 4865041 | ELSTER | Kvarh(Lead/Lag) | 1100 | 999998 | 999998 | 0 | 0 | 0 | 864589 | 869326 | -4737 | -5210700 | -5.2107
21 | DMRC CKT.-II | 4865042 | ELSTER | Kvarh(Lead/Lag) | 1100 | 999999 | 999999 | 0 | 0 | 0 | 900438 | 903442 | -3004 | -3304400 | -3.3044
22 | AKSHARDHAM | 4864943 | ELSTER | Kvarh(Lead/Lag) | 1000 | 996522 | 997235 | -713 | -713000 | -0.713 | 10117 | 10117 | 0 | 0 | 0
| KASHMIRI GATE | [8 empty] | -0.7592 |  |  |  |  | -6.7131
23 | 100 MVA TX.-1 | 4864910 | ELSTER | Kvarh(Lead/Lag) | -1000 | 967111 | 967259 | -148 | 148000 | 0.148 | 980297 | 980473 | -176 | 176000 | 0.176
24 | 100 MVA TX.-2 | 4864911 | ELSTER | Kvarh(Lead/Lag) | -1000 | 986196 | 986545 | -349 | 349000 | 0.349 | 986718 | 987059 | -341 | 341000 | 0.341
25 | B/C (IMP. TO BYPL) | 4902571 | ELSTER | Kvarh(Lead/Lag) | 300 | 2 | 2 | 0 | 0 | 0 | 999951 | 999944 | 7 | 2100 | 0.0021
NARAINA
26 | DMS | 4864830 | ELSTER | Kvarh(Lead/Lag) | 1000 | 893 | 813 | 80 | 80000 | 0.08 | 49311 | 48936 | 375 | 375000 | 0.375
PARK STREET
27 | TX.-1 (66KV) | 4864962 | ELSTER | Kvarh(Lead/Lag) | -1000 | 553 | 556 | -3 | 3000 | 0.003 | 980284 | 980659 | -375 | 375000 | 0.375
28 | TX.-2(66KV) | 4865033 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2960 | 2926 | 34 | -34000 | -0.034 | 984569 | 984408 | 161 | -161000 | -0.161
29 | TX.-1(33KV) | 4864902 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997140 | 997551 | -411 | 411000 | 0.411 | 992132 | 992507 | -375 | 375000 | 0.375
30 | TX.-2(33KV) | 4864935 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998332 | 998583 | -251 | 251000 | 0.251 | 996892 | 997155 | -263 | 263000 | 0.263
IMPORTS
SUBZI MANDI
| O/G BG Rd.1 | 4864808 | ELSTER | Kvarh(Lead/Lag) | 200 | 3536 | 3562 | -26 | -5200 | -0.0052 | 3141 | 3241 | -100 | -20000 | -0.02
32 | O/G BG Rd.2 | 4864841 | ELSTER | Kvarh(Lead/Lag) | 1000 | 12742 | 12536 | 206 | 206000 | 0.206 | 11231 | 10523 | 708 | 708000 | 0.708
RIDGE VALLEY
33 | O/G SHANKAR RD.1 | 4865134 | ELSTER | Kvarh(Lead/Lag) | 100 | 68087 | 67740 | 347 | 34700 | 0.0347 | 1644 | 1644 | 0 | 0 | 0
34 | O/G SHANKAR RD.2 | 4865135 | ELSTER | Kvarh(Lead/Lag) | 100 | 38966 | 35142 | 3824 | 382400 | 0.3824 | 999406 | 999406 | 0 | 0 | 0
| ENERGY INPUT AT 66/33KK LEVEL | [8 empty] | 1.0143 |  |  |  |  | -3.8809
| (A) NET ENERGY TO CENTRAL | [8 empty] | 1.0143 |  |  |  |  | -3.8809
MARCH-2011
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
S.O.W.
1 | Tx.1 | 4864968 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997899 | 998127 | -228 | 228000 | 0.228 | 953907 | 955116 | -1209 | 1209000 | 1.209
2 | Tx.2 | 4864980 | ELSTER | Kvarh(Lead/Lag) | -1000 | 15718 | 15874 | -156 | 156000 | 0.156 | 970810 | 971933 | -1123 | 1123000 | 1.123
3 | Tx.3 | 4864981 | ELSTER | Kvarh(Lead/Lag) | -1000 | 14373 | 14635 | -262 | 262000 | 0.262 | 961778 | 963011 | -1233 | 1233000 | 1.233
PPG
4 | Tx.1 (66 KV) | 4864915 | ELSTER | Kvarh(Lead/Lag) | -1000 | 982873 | 983730 | -857 | 857000 | 0.857 | 993822 | 993839 | -17 | 17000 | 0.017
5 | Tx.2 (66 KV) | 4864993 | ELSTER | Kvarh(Lead/Lag) | -1000 | 974268 | 974439 | -171 | 171000 | 0.171 | 992110 | 992110 | 0 | 0 | 0
6 | 100 MVA Tx.1 (33 KV) | 4864914 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1679 | 1686 | -7 | 7000 | 0.007 | 995143 | 996289 | -1146 | 1146000 | 1.146
7 | 50 MVA Tx.-2 (33 KV) | 4865167 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1502 | 1450 | 52 | -52000 | -0.052 | 985122 | 984996 | 126 | -126000 | -0.126
8 | 50MVA Tx.3 (33 KV) | 4864893 | ELSTER | Kvarh(Lead/Lag) | -1000 | 630 | 676 | -46 | 46000 | 0.046 | 993459 | 995472 | -2013 | 2013000 | 2.013
9 | 100MVA Tx.4 (33 KV) | 4864918 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999750 | 999769 | -19 | 19000 | 0.019 | 979728 | 982171 | -2443 | 2443000 | 2.443
GEETA COLONY
10 | I/C-I | 4864916 | ELSTER | Kvarh(Lead/Lag) | -1000 | 13570 | 13709 | -139 | 139000 | 0.139 | 968077 | 968688 | -611 | 611000 | 0.611
11 | I/C-II | 4864917 | ELSTER | Kvarh(Lead/Lag) | -1000 | 970606 | 970957 | -351 | 351000 | 0.351 | 925070 | 926999 | -1929 | 1929000 | 1.929
GAZIPUR
12 | TX.-1 | 4865053 | ELSTER | Kvarh(Lead/Lag) | -1000 | 20898 | 20898 | 0 | 0 | 0 | 21816 | 21328 | 488 | -488000 | -0.488
13 | TX-2 | 4864986 | ELSTER | Kvarh(Lead/Lag) | -1000 | 14708 | 14708 | 0 | 0 | 0 | 30735 | 29999 | 736 | -736000 | -0.736
SB MILL
14 | ZAKHIRA | 4902528 | ELSTER | Kvarh(Lead/Lag) | 100 | 11525 | 11525 | 0 | 0 | 0 | 4086 | 4086 | 0 | 0 | 0
| ENERGY INPUT AT 66/33/11KV LEVEL | [8 empty] | 2.184 |  |  |  |  | 10.374
| (B) NET ENERGY TO EAST | [8 empty] | 2.184 |  |  |  |  | 10.374
MARCH-2011
BYPL(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
KASHMIRI GATE
1 | CIVIL LINE | 4864889 | ELSTER | Kvarh(Lead/Lag) | -1000 | 992446 | 992474 | -28 | 28000 | 0.028 | 998661 | 998659 | 2 | -2000 | -0.002
2 | CIVIL LINE-2 | 4864800 | ELSTER | Kvarh(Lead/Lag) | -100 | 993740 | 993559 | 181 | -18100 | -0.0181 | 12386 | 12137 | 249 | -24900 | -0.0249 | FINAL READING 28/3/11 DUE TO FAULTY METER
EXPORT TO NDMC
3 | BAIRD RD.1 | 4865136 | ELSTER | Kvarh(Lead/Lag) | -100 | 6329 | 5761 | 568 | -56800 | -0.0568 | 56376 | 54751 | 1625 | -162500 | -0.1625
4 | BAIRD RD.2 | 4865137 | ELSTER | Kvarh(Lead/Lag) | -100 | 11151 | 10383 | 768 | -76800 | -0.0768 | 114025 | 112359 | 1666 | -166600 | -0.1666
5 | NIRMAN BHAWAN | 4865138 | ELSTER | Kvarh(Lead/Lag) | -100 | 995584 | 995584 | 0 | 0 | 0 | 4311 | 4311 | 0 | 0 | 0
6 | H.LANE | 4865139 | ELSTER | Kvarh(Lead/Lag) | -100 | 13501 | 12645 | 856 | -85600 | -0.0856 | 76009 | 74542 | 1467 | -146700 | -0.1467
7 | 66 KV BD MARG-I | 4864948 | ELSTER | Kvarh(Lead/Lag) | -1000 | 38081 | 36667 | 1414 | -1414000 | -1.414 | 232 | 232 | 0 | 0 | 0
8 | 66 KV BD MARG-II | 4864949 | ELSTER | Kvarh(Lead/Lag) |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
EXPORT TO SOUTH & WEST
9 | 66KV R VALLEY-1 | 4864951 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999741 | 999754 | -13 | 13000 | 0.013 | 35621 | 35964 | -343 | 343000 | 0.343
10 | 66KV R VALLEY-2 | 4902501 | ELSTER | Kvarh(Lead/Lag) | -1333.33 | 999651 | 999656 | -5 | 6666.65 | 0.0066666 | 323 | 587 | -264 | 351999.12 | 0.352
EXPORT TO NORTH from SHASTRI PARK
11 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | -1000 | 529 | 520 | 9 | -9000 | -0.009 | 14199 | 13790 | 409 | -409000 | -0.409
12 | PUSA GRID-II | 4864844 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998887 | 998887 | 0 | 0 | 0 | 3516 | 3333 | 183 | -183000 | -0.183
DMS
13 | 33KV PANDAV NGR | 4865169 | ELSTER | Kvarh(Lead/Lag) | -1000 | 607 | 473 | 134 | -134000 | -0.134 | 51056 | 50767 | 289 | -289000 | -0.289
EXCHANGE OF ENERGY 11KV
EXPORTS
B.G.ROAD
14 | CSA | 4902529 | ELSTER | Kvarh(Lead/Lag) | -500 | 3437 | 3421 | 16 | -8000 | -0.008 | 26459 | 26218 | 241 | -120500 | -0.1205
15 | DCM NO.1 | 4902530 | ELSTER | Kvarh(Lead/Lag) | -500 | 3183 | 3166 | 17 | -8500 | -0.0085 | 18011 | 17829 | 182 | -91000 | -0.091
16 | DCM NO.2 | 4902531 | ELSTER | Kvarh(Lead/Lag) | -500 | 3225 | 3208 | 17 | -8500 | -0.0085 | 12176 | 12059 | 117 | -58500 | -0.0585
17 | SADAR S/S | 4902532 | ELSTER | Kvarh(Lead/Lag) | -500 | 3179 | 3165 | 14 | -7000 | -0.007 | 13881 | 13741 | 140 | -70000 | -0.07
KASHMIRI GATE
18 | 20MVA TX. | 4864807 | ELSTER | Kvarh(Lead/Lag) | -100 | 85941 | 84600 | 1341 | -134100 | -0.1341 | 25947 | 25729 | 218 | -21800 | -0.0218
19 | FLY OVER | 4865086 | ELSTER | Kvarh(Lead/Lag) | -100 | 8118 | 7947 | 171 | -17100 | -0.0171 | 28896 | 28045 | 851 | -85100 | -0.0851
D.M.S.
20 | PHILIPS | 4902535 | ELSTER | Kvarh(Lead/Lag) | -100 | 999533 | 999562 | -29 | 2900 | 0.0029 | 4740 | 4724 | 16 | -1600 | -0.0016
21 | 69 NG ROAD | 4902536 | ELSTER | Kvarh(Lead/Lag) | -100 | 2046 | 1817 | 229 | -22900 | -0.0229 | 11593 | 11518 | 75 | -7500 | -0.0075
22 | J BLOCK KIRTI NGR | 4902537 | ELSTER | Kvarh(Lead/Lag) | -100 | 4694 | 4343 | 351 | -35100 | -0.0351 | 44307 | 44121 | 186 | -18600 | -0.0186
23 | H BLOCK | 4902538 | ELSTER | Kvarh(Lead/Lag) | -100 | 8211 | 8079 | 132 | -13200 | -0.0132 | 19022 | 19016 | 6 | -600 | -0.0006
24 | SHADI KHAM PUR | 4902539 | ELSTER | Kvarh(Lead/Lag) | -100 | 999751 | 999783 | -32 | 3200 | 0.0032 | 282 | 283 | -1 | 100 | 0.0001
25 | BREAK FAST | 4902540 | ELSTER | Kvarh(Lead/Lag) | -100 | 15 | 15 | 0 | 0 | 0 | 13398 | 13398 | 0 | 0 | 0
FAIZ ROAD
26 | TIBIA COLLEGE-1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | -100 | 963 | 926 | 37 | -3700 | -0.0037 | 55073 | 54452 | 621 | -62100 | -0.0621
27 | TIBIA COLLEGE-2 | 4902542 | ELSTER | Kvarh(Lead/Lag) | -100 | 673 | 599 | 74 | -7400 | -0.0074 | 49801 | 49491 | 310 | -31000 | -0.031
28 | MANAK PURA | 4902543 | ELSTER | Kvarh(Lead/Lag) | -100 | 898 | 796 | 102 | -10200 | -0.0102 | 71613 | 71027 | 586 | -58600 | -0.0586
[10 empty] | -2.0162 |  |  |  |  | -1.3155
MARCH-2011
EXECUTIVE SUMMARY
ENERGY RELEASED TO CENTRAL
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre A- Page -1) | [8 empty] | 1.0143 |  |  |  |  | -3.8809
| 2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer C Page-3) | [8 empty] | -2.0162 |  |  |  |  | -1.3155
| 3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL.) | [8 empty] | -0.1588 |  |  |  |  | -0.0028
| TOTAL ENERGY TO BSES YAMUNA POWER LTD. - CENTRAL PART | [8 empty] | -1.1607 |  |  |  |  | -5.1992
ENERGY RELEASED TO EAST
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre B- Page -2) | [8 empty] | 2.184 |  |  |  |  | 10.374
| NET ENERGY TO BSES YAMUNA POWER LIMITED | [8 empty] | 1.0233 |  |  |  |  | 5.1748
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 1.0233 | (REACTIVE MUs) |  |  |  | 5.1748 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.15544 | (REACTIVE MUs) |  |  |  | 0.2927 | (REACTIVE MUs)
ASSESSMENT OF BYPL FEEDERS AT GAS TURBINE DMRC-I,DMRC-II,AKSHARDHAM FOR THE PERIOD ( OCT.2010 TO JAN.2011) | [9 empty] | 0.34795 | (REACTIVE MUs) |  |  |  | 8.2784 | (REACTIVE MUs)
[9 empty] | TOTAL | 1.2158 | (REACTIVE MUs) |  |  |  | 13.7459 | (REACTIVE MUs)

## BRPL
DELHI TRANSCO LIMITED | [14 empty] | MARCH-2011
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-BSES RAJDHANI POWER LIMITED
BRPL (+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION
1 | BAY-24 | 4865180 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999169 | 999177 | -8 | -8000 | -0.008 | 11518 | 11625 | -107 | -107000 | -0.107
2 | BAY-25 | 4865095 | ELSTER | Kvarh(Lead/Lag) | 100 | 998736 | 1002887 | -4151 | -415100 | -0.4151 | 680756 | 681309 | -553 | -55300 | -0.0553 | ROLL OVER
3 | BAY-13 | 4865166 | ELSTER | Kvarh(Lead/Lag) | 1000 | 4794 | 4719 | 75 | 75000 | 0.075 | 43456 | 42970 | 486 | 486000 | 0.486
4 | BAY-53 | 4865151 | ELSTER | Kvarh(Lead/Lag) | 1000 | 9547 | 9491 | 56 | 56000 | 0.056 | 605 | 514 | 91 | 91000 | 0.091
5 | BAY-54 | 4865152 | ELSTER | Kvarh(Lead/Lag) | 300 | 441 | 376 | 65 | 19500 | 0.0195 | 250 | 181 | 69 | 20700 | 0.0207
6 | BAY-7 | 4865096 | ELSTER | Kvarh(Lead/Lag) | 100 | 5436 | 4624 | 812 | 81200 | 0.0812 | 79320 | 78193 | 1127 | 112700 | 0.1127
7 | BAY-37 | 4865097 | ELSTER | Kvarh(Lead/Lag) | 100 | 23692 | 22687 | 1005 | 100500 | 0.1005 | 268998 | 268843 | 155 | 15500 | 0.0155
8 | BAY-9 | 4864789 | ELSTER | Kvarh(Lead/Lag) | 100 | 1819 | 1196 | 623 | 62300 | 0.0623 | 329086 | 326360 | 2726 | 272600 | 0.2726
9 | BAY-5 LAJPAT NAGAR | 4865179 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999856 | 999911 | -55 | -55000 | -0.055 | 10641 | 10628 | 13 | 13000 | 0.013
PAAPANKALAN
10 | Tx.1 | 4864973 | ELSTER | Kvarh(Lead/Lag) | -1000 | 995028 | 995463 | -435 | 435000 | 0.435 | 966805 | 967745 | -940 | 940000 | 0.94
11 | Tx.2 | 4864974 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993647 | 994127 | -480 | 480000 | 0.48 | 968929 | 969740 | -811 | 811000 | 0.811
12 | Tx.3 | 4864975 | ELSTER | Kvarh(Lead/Lag) | -1000 | 990649 | 991449 | -800 | 800000 | 0.8 | 959771 | 960706 | -935 | 935000 | 0.935
13 | Tx.4 | 4864976 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999517 | 999290 | 227 | -227000 | -0.227 | 970089 | 970527 | -438 | 438000 | 0.438
PAAPANKALAN-II
14 | Tx.1 | 4864977 | ELSTER | Kvarh(Lead/Lag) | -1000 | 11092 | 9739 | 1353 | -1353000 | -1.353 | 31734 | 31733 | 1 | -1000 | -0.001
15 | Tx.2 | 4865052 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998283 | 998629 | -346 | 346000 | 0.346 | 978850 | 979004 | -154 | 154000 | 0.154
NAJAFGARH
16 | Tx.1 | 4864969 | ELSTER | Kvarh(Lead/Lag) | -1000 | 37609 | 37244 | 365 | -365000 | -0.365 | 27521 | 27536 | -15 | 15000 | 0.015
17 | Tx.2 | 4864970 | ELSTER | Kvarh(Lead/Lag) | -1000 | 3382 | 3746 | -364 | 364000 | 0.364 | 12869 | 13313 | -444 | 444000 | 0.444
18 | Tx.3 | 4864971 | ELSTER | Kvarh(Lead/Lag) | -1000 | 22799 | 22585 | 214 | -214000 | -0.214 | 14403 | 14426 | -23 | 23000 | 0.023
19 | Tx.4 | 4864972 | ELSTER | Kvarh(Lead/Lag) | -1000 | 9297 | 9183 | 114 | -114000 | -0.114 | 40097 | 40123 | -26 | 26000 | 0.026
IMPORT
MANGOLPURI
20 | NANGLOI-1 (03) IMP. | 4864954 | ELSTER | Kvarh(Lead/Lag) | 1000 | 4330 | 4331 | -1 | -1000 | -0.001 | 3697 | 3687 | 10 | 10000 | 0.01
21 | NANGLOI-2 (03) IMP. | 4864955 | ELSTER | Kvarh(Lead/Lag) | 1000 | 5745 | 5741 | 4 | 4000 | 0.004 | 3919 | 3914 | 5 | 5000 | 0.005
LODHI ROAD
22 | Tx.1 | 4864908 | ELSTER | Kvarh(Lead/Lag) | -1000 | 976482 | 978586 | -2104 | 2104000 | 2.104 | 910094 | 910094 | 0 | 0 | 0
23 | Tx.2 | 4864909 | ELSTER | Kvarh(Lead/Lag) | -1000 | 994478 | 995294 | -816 | 816000 | 0.816 | 887629 | 887818 | -189 | 189000 | 0.189
OKHLA
24 | Tx.1 (66 KV) | 4864964 | ELSTER | Kvarh(Lead/Lag) | -1000 | 307 | 307 | 0 | 0 | 0 | 2910 | 5133 | -2223 | 2223000 | 2.223
25 | Tx.2 (66 KV) | 4864965 | ELSTER | Kvarh(Lead/Lag) | -1000 | 448 | 448 | 0 | 0 | 0 | 995557 | 997796 | -2239 | 2239000 | 2.239
26 | Tx.1 (33 KV) | 4864890 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997750 | 997538 | 212 | -212000 | -0.212 | 959548 | 959570 | -22 | 22000 | 0.022
27 | Tx.2 (33 KV) | 4864891 | ELSTER | Kvarh(Lead/Lag) | -1000 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | OFF
28 | Tx.3 (33 KV) | 4864906 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999631 | 999631 | 0 | 0 | 0 | 954100 | 956714 | -2614 | 2614000 | 2.614
29 | Tx.4 (33 KV) | 4864907 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999031 | 999031 | 0 | 0 | 0 | 946468 | 949914 | -3446 | 3446000 | 3.446
BRPL(+) continue | [14 empty] | MARCH-2011
VASANT KUNJ
30 | Tx.1 | 4864988 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998778 | 999042 | -264 | 264000 | 0.264 | 977134 | 978307 | -1173 | 1173000 | 1.173
31 | Tx.2 | 4864989 | ELSTER | Kvarh(Lead/Lag) | -1000 | 22 | 286 | -264 | 264000 | 0.264 | 993729 | 994895 | -1166 | 1166000 | 1.166
32 | Tx.3 | 4864979 | ELSTER | Kvarh(Lead/Lag) | -2000 | 989863 | 989849 | 14 | -28000 | -0.028 | 981402 | 981320 | 82 | -164000 | -0.164
MEHRAULI
33 | Tx.1 | 4864966 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998261 | 998328 | -67 | 67000 | 0.067 | 948551 | 948988 | -437 | 437000 | 0.437
34 | Tx.2 | 4864967 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1007 | 1048 | -41 | 41000 | 0.041 | 964038 | 965444 | -1406 | 1406000 | 1.406
35 | Tx.3 | 4865048 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998482 | 998545 | -63 | 63000 | 0.063 | 954226 | 955232 | -1006 | 1006000 | 1.006
RIDGE VALLEY
36 | Tx-1 | 4864827 | ELSTER | Kvarh(Lead/Lag) | -666.666 | 783 | 783 | 0 | 0 | 0 | 597 | 597 | 0 | 0 | 0
37 | Tx-2 | 4864828 | ELSTER | Kvarh(Lead/Lag) | -666.666 | 993260 | 995841 | -2581 | 1720664.946 | 1.7207 | 997307 | 998940 | -1633 | 1088665.578 | 1.0887
DIAL
38 | Tx-1 | 4865024 | ELSTER | Kvarh(Lead/Lag) | -2000 | 161 | 133 | 28 | -56000 | -0.056 | 451 | 269 | 182 | -364000 | -0.364
39 | Tx-2 | 4864920 | ELSTER | Kvarh(Lead/Lag) | -2000 | 996871 | 996840 | 31 | -62000 | -0.062 | 999777 | 999615 | 162 | -324000 | -0.324
PARK STREET
40 | 66KV R VALLEY-1 | 4864951 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999741 | 999754 | -13 | -13000 | -0.013 | 35621 | 35964 | -343 | -343000 | -0.343
41 | 66KV R VALLEY-2 | 4902501 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 999651 | 999656 | -5 | -6666.65 | -0.0066666 | 323 | 587 | -264 | -351999.12 | -0.352
SARITA VIHAR
42 | TX-1 | 4864990 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2846 | 1948 | 898 | -898000 | -0.898 | 982001 | 982016 | -15 | 15000 | 0.015
43 | Tx-2 | 4864991 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999110 | 999226 | -116 | 116000 | 0.116 | 988192 | 988308 | -116 | 116000 | 0.116
NARAINA
44 | GOPI NATH BAZAAR | 4865092 | ELSTER | Kvarh(Lead/Lag) | 100 | 4214 | 4111 | 103 | 10300 | 0.0103 | 7583 | 7556 | 27 | 2700 | 0.0027
SUDARSHAN PARK
45 | VISHAL | 4864792 | ELSTER | Kvarh(Lead/Lag) | 100 | 36227 | 34534 | 1693 | 169300 | 0.1693 | 146577 | 147860 | -1283 | -128300 | -0.1283
REWARI LINE
46 | 33KV B/C | 4865170 | ELSTER | Kvarh(Lead/Lag) | 1000 | 0 | 0 | 0 | 0 | 0 | 999975 | 999975 | 0 | 0 | 0
KANJAWALA
47 | 66KV DMRC | 4864961 | ELSTER | Kvarh(Lead/Lag) | 1000 | 983068 | 983494 | -426 | -426000 | -0.426 | 993320 | 993647 | -327 | -327000 | -0.327
A.I.I.M.S.
48 | 11KV VIKAS SADAN | 4902586 | ELSTER | Kvarh(Lead/Lag) | 100 | 999473 | 999476 | -3 | -300 | -0.0003 | 1101 | 1070 | 31 | 3100 | 0.0031
49 | 11KV NDSE | 4902587 | ELSTER | Kvarh(Lead/Lag) | 100 | 2865 | 2431 | 434 | 43400 | 0.0434 | 3599 | 3342 | 257 | 25700 | 0.0257
66KV GHEBRA
50 | GHEBRA-NANGLOI | 4902502 | ELSTER | Kvarh(Lead/Lag) | 1250 | 998227 | 998396 | -169 | -211250 | -0.21125 | 999974 | 999841 | 133 | 166250 | 0.16625 | LOADED ON 04/03/2011
SUM OF ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | 3.8368 |  |  |  |  | 19.9853
BRPL (-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 % |  |  | MARCH-2011
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TILAK MARG
1 | EXHB-II | 4865143 | ELSTER | Kvarh(Lead/Lag) | 100 | 980806 | 983755 | -2949 | -294900 | -0.2949 | 858865 | 859235 | -370 | -37000 | -0.037
EXPORT TO EAST & CENTRE
RIDGE VALLEY
2 | O/G SHANKAR RD.1 | 4865134 | ELSTER | Kvarh(Lead/Lag) | -100 | 68087 | 67740 | 347 | -34700 | -0.0347 | 1644 | 1644 | 0 | 0 | 0
3 | O/G SHANKAR RD.2 | 4865135 | ELSTER | Kvarh(Lead/Lag) | -100 | 38966 | 35142 | 3824 | -382400 | -0.3824 | 999406 | 999406 | 0 | 0 | 0
4 | KHYBER LANE-1 EXP. | 4864804 | ELSTER | Kvarh(Lead/Lag) | -100 | 337 | 337 | 0 | 0 | 0 | 999974 | 999974 | 0 | 0 | 0
5 | KHYBER LANE-2 EXP. | 4865163 | ELSTER | Kvarh(Lead/Lag) | -100 | 562 | 562 | 0 | 0 | 0 | 999997 | 999997 | 0 | 0 | 0
EXPORTS(*)
EXPORT TO NDMC
6 | SPM NO.1 | 4865140 | ELSTER | Kvarh(Lead/Lag) | -100 | 705618 | 693017 | 12601 | -1260100 | -1.2601 | 43485 | 43485 | 0 | 0 | 0
7 | SPM NO.2 | 4864852 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2599 | 2174 | 425 | -425000 | -0.425 | 935 | 908 | 27 | -27000 | -0.027
8 | NEHRU PARK | 4865142 | ELSTER | Kvarh(Lead/Lag) | -100 | 719509 | 703984 | 15525 | -1552500 | -1.5525 | 38222 | 38222 | 0 | 0 | 0
EXPORT TO NDMC
9 | SHAN NAGAR 1 | 4865093 | ELSTER | Kvarh(Lead/Lag) | -100 | 13278 | 10831 | 2447 | -244700 | -0.2447 | 48622 | 48622 | 0 | 0 | 0
10 | SHAN NAGAR 2 | 4865094 | ELSTER | Kvarh(Lead/Lag) | -100 | 13329 | 12007 | 1322 | -132200 | -0.1322 | 47642 | 47390 | 252 | -25200 | -0.0252
11 | VIDYUT BHAWAN | 4865144 | ELSTER | Kvarh(Lead/Lag) | -200 | 31508 | 31266 | 242 | -48400 | -0.0484 | 100697 | 100688 | 9 | -1800 | -0.0018 | CT RATIO FOUND 800/5 IN CT RATIO TESTING SO M.F. IS DOUBLED
EXPORTS(*)
A.I.I.M.S.
12 | TRANSFORMER-1 | 4865103 | ELSTER | Kvarh(Lead/Lag) | -100 | 13240 | 11613 | 1627 | -162700 | -0.1627 | 2451 | 2413 | 38 | -3800 | -0.0038
13 | TRANSFORMER-2 | 4865132 | ELSTER | Kvarh(Lead/Lag) | -100 | 12710 | 10476 | 2234 | -223400 | -0.2234 | 606081 | 603832 | 2249 | -224900 | -0.2249
14 | TRANSFORMER-3 | 4864803 | ELSTER | Kvarh(Lead/Lag) | -100 | 84571 | 82092 | 2479 | -247900 | -0.2479 | 165295 | 162638 | 2657 | -265700 | -0.2657
KIDWAI NAGAR
15 | TR(10MVA)KILOKRI#2 | 4865133 | ELSTER | Kvarh(Lead/Lag) | 100 | 154597 | 149182 | 5415 | 541500 | 0.5415 | 25378 | 24913 | 465 | 46500 | 0.0465
EXHIBITION I
16 | TILAK MARG | 4865076 | ELSTER | Kvarh(Lead/Lag) | -100 | 728 | 672 | 56 | -5600 | -0.0056 | 11343 | 11153 | 190 | -19000 | -0.019
17 | KRISHI BHAWAN | 4865077 | ELSTER | Kvarh(Lead/Lag) | -100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
REWARI LINE (ENERGY EXCHANGE WITH NDPL)
18 | 20 MVA TX.-2(Delv.) | 4864824 | ELSTER | Kvarh(Lead/Lag) | -100 | 9192 | 8898 | 294 | -29400 | -0.0294 | 44885 | 44377 | 508 | -50800 | -0.0508
EXCHANGE OF ENERGY 11KV
EXPORTS
VISHAL
19 | RAMESH NAGAR-1 | 4865090 | ELSTER | Kvarh(Lead/Lag) | -100 | 6231 | 6042 | 189 | -18900 | -0.0189 | 8141 | 7171 | 970 | -97000 | -0.097
20 | BALI NAGAR -1 | 4902519 | ELSTER | Kvarh(Lead/Lag) | -100 | 8264 | 8245 | 19 | -1900 | -0.0019 | 26496 | 25662 | 834 | -83400 | -0.0834
21 | ESI HOSPITAL | 4902520 | ELSTER | Kvarh(Lead/Lag) | -100 | 13706 | 13613 | 93 | -9300 | -0.0093 | 35231 | 34647 | 584 | -58400 | -0.0584
S.B.MILL
22 | MOTI NAGAR KIOSK | 4902521 | ELSTER | Kvarh(Lead/Lag) | -100 | 28912 | 28353 | 559 | -55900 | -0.0559 | 8523 | 8523 | 0 | 0 | 0
23 | 53 RAMA ROAD | 4902522 | ELSTER | Kvarh(Lead/Lag) | -100 | 840 | 840 | 0 | 0 | 0 | 185 | 185 | 0 | 0 | 0
24 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | -100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
25 | 70 RAMA ROAD | 4902524 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | MOTI NAGAR 2 | 4902525 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | NAJAFGARH ROAD | 4902526 | ELSTER | Kvarh(Lead/Lag) | -100 | 13825 | 13371 | 454 | -45400 | -0.0454 | 8414 | 8346 | 68 | -6800 | -0.0068
28 | PHILIPS | 4902527 | ELSTER | Kvarh(Lead/Lag) | -100 | 997829 | 997815 | 14 | -1400 | -0.0014 | 999975 | 999975 | 0 | 0 | 0
29 | ZAKHIRA | 4902528 | ELSTER | Kvarh(Lead/Lag) | -100 | 11525 | 11525 | 0 | 0 | 0 | 4086 | 4086 | 0 | 0 | 0
REWARI LINE (11KV TRANSFER OF ENERGY)
30 | BSES -NDPL(EX.) ON BUS-1&2 | 4902514 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | METER FAULTY
30 | BSES -NDPL(EX.) ON BUS-1&2 | 4865087 | ELSTER | Kvarh(Lead/Lag) | 400 | 4567 | 4567 | 0 | 0 | 0 | 12600 | 12592 | 8 | 3200 | 0.0032 | INSTALLED ON 23/03/11 AGAINST DEFECTIVE MTR. 4902514
31 | BSES -NDPL(EX.) ON BUS-2&3 | 4902516 | ELSTER | Kvarh(Lead/Lag) | -100 | 999377 | 999472 | -95 | 9500 | 0.0095 | 999145 | 999160 | -15 | 1500 | 0.0015
TOTAL OF ENERGY AT INTER COMPANY EXCHANGE POINTS | [9 empty] | -4.6257 |  |  |  |  | -0.8496
MARCH-2011
EXECUTIVE SUMMERY BSES R.P. LTD.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (REFER SHEET BRPL (+)) | [9 empty] | 3.8368 |  |  |  |  | 19.9853
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet BRPL(-)) | [9 empty] | -4.6257 |  |  |  |  | -0.8496
3)ENERGY RECEIVED FROM ROHTAK ROAD (REFER ROHTAK ROAD SHEET ENC.) | [9 empty] | 0.9246 |  |  |  |  | 0.9592
4) ENERGY RELEASED TO MES BY BRPL | [9 empty] | -0.3713 |  |  |  |  | -0.0978
NET ENERGY TO BSES RAJDHANI POWER LIMITED | [9 empty] | -0.23555 |  |  |  |  | 19.9971
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | -0.23555 | (REACTIVE MUs) |  |  |  | 19.9971 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.25699 | (REACTIVE MUs) |  |  |  | 0.48393 | (REACTIVE MUs)
ASSESSMENT OF BYPL FEEDERS AT GAS TURBINE DMRC-I,DMRC-II,AKSHARDHAM FOR THE PERIOD ( OCT.2010 TO JAN.2011) | [9 empty] | 0.60725 | (REACTIVE MUs) |  |  |  | 14.3997 | (REACTIVE MUs)
ASSESSMENT OF VIDYUT BHAWAN LODHI ROAD FOR PERIOD OF APRIL-2010 TO JAN.2011 | [9 empty] | -0.3194 | (REACTIVE MUs) |  |  |  | -1.9801 | (REACTIVE MUs)
[9 empty] | TOTAL | -0.20469 | (REACTIVE MUs) |  |  |  | 32.9007 | (REACTIVE MUs)

## NDMC
DELHI TRANSCO LIMITED | [15 empty] | MARCH-2011
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-NDMC
NDMC(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
AT PARK STREET
EXPORT TO NDMC
1 | BAIRD RD.1 | 4865136 | ELSTER | Kvarh(Lead/Lag) | 100 | 6329 | 5761 | 568 | 56800 | 0.0568 | 56376 | 54751 | 1625 | 162500 | 0.1625
2 | BAIRD RD.2 | 4865137 | ELSTER | Kvarh(Lead/Lag) | 100 | 11151 | 10383 | 768 | 76800 | 0.0768 | 114025 | 112359 | 1666 | 166600 | 0.1666
3 | NIRMAN BHAWAN | 4865138 | ELSTER | Kvarh(Lead/Lag) | 100 | 995584 | 995584 | 0 | 0 | 0 | 4311 | 4311 | 0 | 0 | 0
4 | H.LANE | 4865139 | ELSTER | Kvarh(Lead/Lag) | 100 | 13501 | 12645 | 856 | 85600 | 0.0856 | 76009 | 74542 | 1467 | 146700 | 0.1467
5 | 66 KV BD MARG-I | 4864948 | ELSTER | Kvarh(Lead/Lag) | 1000 | 38081 | 36667 | 1414 | 1414000 | 1.414 | 232 | 232 | 0 | 0 | 0
6 | 66 KV BD MARG-II | 4864949 | ELSTER | Kvarh(Lead/Lag) |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
I.P.STATION
EXPORT TO NDMC
6 | BAY-2 (N BWN) | 4865124 | ELSTER | Kvarh(Lead/Lag) | 100 | 997827 | 998007 | -180 | -18000 | -0.018 | 268805 | 268403 | 402 | 40200 | 0.0402
7 | BAY-4 (E LANE) | 4865125 | ELSTER | Kvarh(Lead/Lag) | 100 | 3458 | 3297 | 161 | 16100 | 0.0161 | 400708 | 398282 | 2426 | 242600 | 0.2426
8 | BAY-6 (T MARG) | 4865126 | ELSTER | Kvarh(Lead/Lag) | 100 | 7945 | 6852 | 1093 | 109300 | 0.1093 | 179582 | 178570 | 1012 | 101200 | 0.1012
9 | BAY-10 (E LANE) | 4865127 | ELSTER | Kvarh(Lead/Lag) | 100 | 3868 | 3643 | 225 | 22500 | 0.0225 | 294480 | 291887 | 2593 | 259300 | 0.2593
10 | BAY-16 (N BWN) | 4865128 | ELSTER | Kvarh(Lead/Lag) | 100 | 998852 | 998971 | -119 | -11900 | -0.0119 | 201239 | 199204 | 2035 | 203500 | 0.2035
11 | BAY-28 (C PLACE) | 4865129 | ELSTER | Kvarh(Lead/Lag) | 100 | 998489 | 998773 | -284 | -28400 | -0.0284 | 122729 | 123009 | -280 | -28000 | -0.028 | ROLL OVER
12 | BAY-38 (C PLACE) | 4865130 | ELSTER | Kvarh(Lead/Lag) | 100 | 7989 | 7295 | 694 | 69400 | 0.0694 | 180093 | 177728 | 2365 | 236500 | 0.2365
13 | BAY-42 (C PLACE) | 4865131 | ELSTER | Kvarh(Lead/Lag) | 100 | 6420 | 6042 | 378 | 37800 | 0.0378 | 218019 | 216806 | 1213 | 121300 | 0.1213
G.T.
14 | VIDYUT BHAWAN-1 | 4865037 | ELSTER | Kvarh(Lead/Lag) | 1100 | 0 | 0 | 0 | 0 | 0 | 48879 | 47492 | 1387 | 1525700 | 1.5257
15 | VIDYUT BHAWAN-2 | 4865038 | ELSTER | Kvarh(Lead/Lag) | 1000 | 5168 | 4948 | 220 | 220000 | 0.22 | 36122 | 36121 | 1 | 1000 | 0.001
16 | SCHOOL LANE-1 | 4865039 | ELSTER | Kvarh(Lead/Lag) | 1100 | 0 | 0 | 0 | 0 | 0 | 118071 | 116608 | 1463 | 1609300 | 1.6093
17 | SCHOOL LANE-2 | 4865040 | ELSTER | Kvarh(Lead/Lag) | 1000 | 7674 | 7646 | 28 | 28000 | 0.028 | 48093 | 48092 | 1 | 1000 | 0.001
[10 empty] | 0.248 |  |  |  |  | 3.137
RIDGE VALLEY
18 | SPM NO.1 | 4865140 | ELSTER | Kvarh(Lead/Lag) | 100 | 705618 | 693017 | 12601 | 1260100 | 1.2601 | 43485 | 43485 | 0 | 0 | 0
19 | SPM NO.2 | 4864852 | ELSTER | Kvarh(Lead/Lag) | 1000 | 2599 | 2174 | 425 | 425000 | 0.425 | 935 | 908 | 27 | 27000 | 0.027
20 | NEHRU PARK | 4865142 | ELSTER | Kvarh(Lead/Lag) | 100 | 719509 | 703984 | 15525 | 1552500 | 1.5525 | 38222 | 38222 | 0 | 0 | 0
A.I.I.M.S.
21 | TX-I | 4865103 | ELSTER | Kvarh(Lag) | 100 | 13240 | 11613 | 1627 | 162700 | 0.1627 | 2451 | 2413 | 38 | 3800 | 0.0038
22 | TX-2 | 4865132 | ELSTER | Kvarh(Lead/Lag) | 100 | 12710 | 10476 | 2234 | 223400 | 0.2234 | 606081 | 603832 | 2249 | 224900 | 0.2249
23 | TX-3 | 4864803 | ELSTER | Kvarh(Lead/Lag) | 100 | 84571 | 82092 | 2479 | 247900 | 0.2479 | 165295 | 162638 | 2657 | 265700 | 0.2657
MARCH-2011
NDMC(+) Continue…
KIDWAI NAGAR
24 | TR(10MVA) KILOKRI#2 | 4865133 | ELSTER | Kvarh(Lead/Lag) | -100 | 154597 | 149182 | 5415 | -541500 | -0.5415 | 25378 | 24913 | 465 | -46500 | -0.0465
EXHIBITION I
25 | TILAK MARG | 4865076 | ELSTER | Kvarh(Lead/Lag) | 100 | 728 | 672 | 56 | 5600 | 0.0056 | 11343 | 11153 | 190 | 19000 | 0.019
26 | KRISHI BHAWAN | 4865077 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
LODHI ROAD
27 | SHAN NAGAR 1 | 4865093 | ELSTER | Kvarh(Lead/Lag) | 100 | 13278 | 10831 | 2447 | 244700 | 0.2447 | 48622 | 48622 | 0 | 0 | 0
28 | SHAN NAGAR 2 | 4865094 | ELSTER | Kvarh(Lead/Lag) | 100 | 13329 | 12007 | 1322 | 132200 | 0.1322 | 47642 | 47390 | 252 | 25200 | 0.0252
29 | VIDYUT BHAWAN (exp) | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 31508 | 31266 | 242 | 48400 | 0.0484 | 100697 | 100688 | 9 | 1800 | 0.0018 | CT RATIO FOUND 800/5 IN CT RATIO TESTING SO M.F. IS DOUBLED
TILAK MARG
30 | EXHB-II | 4865143 | ELSTER | Kvarh(Lag) | -100 | 980806 | 983755 | -2949 | 294900 | 0.2949 | 858865 | 859235 | -370 | 37000 | 0.037
NDMC(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
AIIMS
1 | 11KV VIKAS SADAN | 4902586 | ELSTER | Kvarh(Lead/Lag) | -100 | 999473 | 999476 | -3 | 300 | 0.0003 | 1101 | 1070 | 31 | -3100 | -0.0031
2 | 11KV NDSE | 4902587 | ELSTER | Kvarh(Lead/Lag) | -100 | 2865 | 2431 | 434 | -43400 | -0.0434 | 3599 | 3342 | 257 | -25700 | -0.0257
TOTAL ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | 6.0908 |  |  |  |  | 5.3185
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
ENERGY TO NDMC | [9 empty] | 6.0908 |  |  |  |  | 5.3185
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.040839 |  |  |  |  | 0.076904
ASSESSMENT OF BYPL FEEDERS AT GAS TURBINE DMRC-I,DMRC-II,AKSHARDHAM FOR THE PERIOD ( OCT.2010 TO JAN.2011) | [9 empty] | 0.078744 |  |  |  |  | 1.8373
ASSESSMENT OF VIDYUT BHAWAN LODHI ROAD FOR PERIOD OF APRIL-2010 TO JAN.2011 | [9 empty] | 0.3194 |  |  |  |  | 1.9801
TOTAL ENERGY TO NDMC | [9 empty] | 6.4481 |  |  |  |  | 9.2128

## MES
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | MARCH-2011
CUSTOMER- MES
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
MES(+)
FED FROM DTL SYSTEM.
NARAINA ( ON 33KV)
1 | KHBR LANE-1-EXP. | 4864848 | ELSTER | Kvarh(Lead/Lag) | 1000 | 538 | 511 | 27 | 27000 | 0.027 | 12154 | 12062 | 92 | 92000 | 0.092
2 | KHBR LANE-2 -EXP. | 4864849 | ELSTER | Kvarh(Lead/Lag) | 1000 | 369 | 349 | 20 | 20000 | 0.02 | 16519 | 16439 | 80 | 80000 | 0.08
3 | KIRBY PLACE-1 | 4864846 | ELSTER | Kvarh(Lead/Lag) | 1000 | 651 | 610 | 41 | 41000 | 0.041 | 23615 | 23528 | 87 | 87000 | 0.087
4 | KIRBY PLACE-2 | 4864847 | ELSTER | Kvarh(Lead/Lag) | 1000 | 404 | 386 | 18 | 18000 | 0.018 | 12372 | 12309 | 63 | 63000 | 0.063
5 | SHEKHAWATI | 4864850 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1174 | 1098 | 76 | 76000 | 0.076 | 6045 | 6031 | 14 | 14000 | 0.014
RIDGE VALLEY ON 33KV
6 | KHBR LANE-1 -EXP | 4864804 | ELSTER | Kvarh(Lead/Lag) | 100 | 337 | 337 | 0 | 0 | 0 | 999974 | 999974 | 0 | 0 | 0
7 | KHBR LANE-2 -EXP. | 4865163 | ELSTER | Kvarh(Lead/Lag) | 100 | 562 | 562 | 0 | 0 | 0 | 999997 | 999997 | 0 | 0 | 0
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | 0.182 |  |  |  |  | 0.336
FED FROM BSES RAJDHANI POWER LIMITED (11KV)
8 | SIGNAL ENCLAVE | 4865065 | ELSTER | Kvarh(Lead/Lag) | 100 | 3211 | 3211 | 0 | 0 | 0 | 32058 | 32040 | 18 | 1800 | 0.0018
9 | R.R. HOSPITAL | 4865066 | ELSTER | Kvarh(Lead/Lag) | 100 | 22944 | 21669 | 1275 | 127500 | 0.1275 | 52448 | 52240 | 208 | 20800 | 0.0208
10 | DEFENCE CLUB | 4865067 | ELSTER | Kvarh(Lead/Lag) | 100 | 63249 | 62966 | 283 | 28300 | 0.0283 | 5552 | 5462 | 90 | 9000 | 0.009
11 | SUBROTO PARK | 4865078 | ELSTER | Kvarh(Lead/Lag) | 100 | 14712 | 13126 | 1586 | 158600 | 0.1586 | 36949 | 36840 | 109 | 10900 | 0.0109
12 | SUBROTO PARK | 4865079 | ELSTER | Kvarh(Lead/Lag) | 100 | 999777 | 999778 | -1 | -100 | -0.0001 | 13926 | 13830 | 96 | 9600 | 0.0096
13 | BI LINES | 4865080 | ELSTER | Kvarh(Lead/Lag) | 100 | 68611 | 68041 | 570 | 57000 | 0.057 | 28495 | 28041 | 454 | 45400 | 0.0454
14 | BI LINES | 4865081 | ELSTER | Kvarh(Lead/Lag) | 100 | 643 | 643 | 0 | 0 | 0 | 1048 | 1045 | 3 | 300 | 0.0003
TOTAL FED FROM BSES RAJDHANI POWER LIMITED (11KV) | [9 empty] | 0.3713 |  |  |  |  | 0.0978
MES(-)
FED TO BSES RAJDHANI POWER LIMITED (11KV)
15 | BOOSTER PUMP | 4902545 | ELSTER | Kvarh(Lead/Lag) | 50 | 7449 | 7449 | 0 | 0 | 0 | 18541 | 18541 | 0 | 0 | 0
TOTAL FED TO BSES RAJDHANI POWER LIMITED (11KV) | [9 empty] | 0 |  |  |  |  | 0
| TOTAL FED FROM BSES RAJDHANI POWER LIMITED (11KV) | [8 empty] | 0.3713 |  |  |  |  | 0.0978
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | 0.182 |  |  |  |  | 0.336
| GRAND TOTAL (BSES RPL+NDPL+DTL) | [8 empty] | 0.5533 |  |  |  |  | 0.4338
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 0.5533 | (REACTIVE MUs) |  |  |  | 0.4338 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.005231 | (REACTIVE MUs) |  |  |  | 0.0098504 | (REACTIVE MUs)
ASSESSMENT OF BYPL FEEDERS AT GAS TURBINE (DMRC-I,DMRC-II,AKSHARDHAM) | [9 empty] | 0.014169 |  |  |  |  | 0.32535
FOR THE PERIOD APRIL 2010 TO SEP.2010
[9 empty] | TOTAL | 0.56224 | (REACTIVE MUs) |  |  |  | 0.769 | (REACTIVE MUs)

## ROHTAK ROAD
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | MARCH-2011
ROHTAK ROAD
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TO BSES RAJDHANI
AT 33 KV LEVEL
1 | O/G SBMILL-1 | 4864796 | ELSTER | Kvarh(Lead/Lag) | 100 | 70120 | 66676 | 3444 | 344400 | 0.3444 | 76607 | 76557 | 50 | 5000 | 0.005
2 | O/G SBMILL-2 | 4864797 | ELSTER | Kvarh(Lead/Lag) | 100 | 13659 | 14678 | -1019 | -101900 | -0.1019 | 999939 | 999957 | -18 | -1800 | -0.0018
3 | O/G VISHAL-1 | 4864818 | ELSTER | Kvarh(Lead/Lag) | 100 | 132957 | 130531 | 2426 | 242600 | 0.2426 | 86465 | 86284 | 181 | 18100 | 0.0181
4 | O/G MADI PUR | 4864842 | ELSTER | Kvarh(Lead/Lag) | 1000 | 13085 | 12678 | 407 | 407000 | 0.407 | 16889 | 16862 | 27 | 27000 | 0.027
AT 33/11 KV LEVEL
5 | TX.-I | 4864880 | ELSTER | Kvarh(Lead/Lag) | -500 | 993912 | 993950 | -38 | 19000 | 0.019 | 959780 | 960805 | -1025 | 512500 | 0.5125
6 | TX-II | 4864881 | ELSTER | Kvarh(Lead/Lag) | -500 | 994466 | 994493 | -27 | 13500 | 0.0135 | 989368 | 990166 | -798 | 399000 | 0.399
7 | B/C (IMP.TO BRPL) | 4902572 | ELSTER | Kvarh(Lead/Lag) | 300 | 999989 | 999989 | 0 | 0 | 0 | 999904 | 999906 | -2 | -600 | -0.0006
| TOTAL BSES RAJDHANI PO.LTD. | [8 empty] | 0.9246 |  |  |  |  | 0.9592
TO BSES YAMUNA PO. LTD.
AT 33 KV LEVEL
8 | O/G FAIZ ROAD | 4864794 | ELSTER | Kvarh(Lead/Lag) | 200 | 959581 | 960749 | -1168 | -233600 | -0.2336 | 990930 | 990954 | -24 | -4800 | -0.0048
9 | O/G DMS | 4864795 | ELSTER | Kvarh(Lead/Lag) | 100 | 930472 | 929724 | 748 | 74800 | 0.0748 | 931332 | 931312 | 20 | 2000 | 0.002
| TOTAL (BSES Y.P.L.) | [8 empty] | -0.1588 |  |  |  |  | -0.0028
TO NORTH DELHI POWER LIMITED
AT 33 KV LEVEL
10 | O/G VISHAL-2 | 4864819 | ELSTER | Kvarh(Lead/Lag) | 200 | 150759 | 147178 | 3581 | 716200 | 0.7162 | 252424 | 252080 | 344 | 68800 | 0.0688
11 | O/G 33KV RAMPURA-1 | 4864801 | ELSTER | Kvarh(Lead/Lag) | 200 | 28477 | 25463 | 3014 | 602800 | 0.6028 | 38987 | 38975 | 12 | 2400 | 0.0024
12 | O/G 33KV RAMPURA-2 | 4864820 | ELSTER | Kvarh(Lead/Lag) | 100 | 25174 | 19249 | 5925 | 592500 | 0.5925 | 67695 | 67670 | 25 | 2500 | 0.0025
13 | O/G 33KV SH.W.BAGH-I | 4865168 | ELSTER | Kvarh(Lead/Lag) | 1000 | 991137 | 991507 | -370 | -370000 | -0.37 | 997644 | 997644 | 0 | 0 | 0
14 | O/G 33KV SH.W.BAGH-2 | 4864802 | ELSTER | Kvarh(Lead/Lag) | 100 | 985169 | 985969 | -800 | -80000 | -0.08 | 7832 | 7839 | -7 | -700 | -0.0007
| O/G 33KV KIRTI NAGAR | 5128400 | ELSTER | Kvarh(Lead/Lag) | -937.5 | 147 | 132 | 15 | -14062.5 | -0.014063 | 45 | 32 | 13 | -12187.5 | -0.012188 | IN RECEIVED MODE FROM 12/3/11 TO 22/3/11
15 | O/G 33KV KIRTI NAGAR | 5128400 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 144 | 147 | -3 | -2812.5 | -0.0028125 | 35 | 45 | -10 | -9375 | -0.009375
AT 33/11 KV LEVEL
16 | TX-III | 4864882 | ELSTER | Kvarh(Lead/Lag) | -500 | 994859 | 995285 | -426 | 213000 | 0.213 | 995902 | 995906 | -4 | 2000 | 0.002
17 | B/C (IMP.TO NDPL) | 4902572 | ELSTER | Kvarh(Lead/Lag) | -300 | 999989 | 999989 | 0 | 0 | 0 | 999904 | 999906 | -2 | 600 | 0.0006
| TOTAL NDPL | [8 empty] | 1.6576 |  |  |  |  | 0.054038
| E) NET EXPORT TO BSES RPL | [8 empty] | 0.9246 |  |  |  |  | 0.9592
| F) NET EXPORT TO BSES YPL | [8 empty] | -0.1588 |  |  |  |  | -0.0028
| G) NET EXPORT TO N.D.P.L. | [8 empty] | 1.6576 |  |  |  |  | 0.054038

## STEPPED UP GENCO
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | MARCH-2011
A.) EXPORT/IMPORT OF REACTIVE ENERGY IN LEAD/LAG MODE ON IBT's AT GENCO
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | REMARK
G.T.
| (66KV ) | (EXPORT)
1 | IBT-I | 4902497 | ELSTER | kvarh (Lead/lag) | 2000 | 6759 | 6455 | 304 | 608000 | 0.608 | 999918 | 999918 | 0 | 0 | 0
2 | IBT-2 | 4902498 | ELSTER | kvarh (Lead/lag) | 2000 | 5752 | 5466 | 286 | 572000 | 0.572 | 999699 | 999698 | 1 | 2000 | 0.002
[7 empty] | NET REACTIVE ENERGY |  |  | 1.18 |  | NET REACTIVE ENERGY |  |  | 0.002
RPH
| (33KV ) | (EXPORT)
3 | IBT-I | 4902505 | ELSTER | kvarh (Lead/lag) | 1000 | 999658 | 999677 | -19 | -19000 | -0.019 | 42182 | 41591 | 591 | 591000 | 0.591
4 | IBT-2 | 4902506 | ELSTER | kvarh (Lead/lag) | 1000 | 991408 | 991412 | -4 | -4000 | -0.004 | 987320 | 985553 | 1767 | 1767000 | 1.767
[7 empty] | NET REACTIVE ENERGY |  |  | -0.023 |  | NET REACTIVE ENERGY |  |  | 2.358
1)TOTAL NET REACTIVE ENERGY FROM GENCO AT 66/33KV LEVEL | [9 empty] | 1.157 |  |  |  |  | 2.36
B) | REACTIVE ENERGY DRAWL ON FEEDERS FROM GENCO BY
[7 empty] | NDPL = |  |  | 0 |  |  |  |  | 0
[7 empty] | BRPL = |  |  | 0 |  |  |  |  | 0
[7 empty] | BYPL = |  |  | -0.7592 |  |  |  |  | -6.7131
[7 empty] | NDMC = |  |  | 0.248 |  |  |  |  | 3.137
MES =
[7 empty] | 2)TOTAL |  |  | -0.5112 |  |  |  |  | -3.5761
C) TOTAL REACTIVE ENERGY TO BE DISTRIBUTED AMONGS DISCOMs [1+2]= | [9 empty] | 0.6458 |  |  |  |  | -1.2161
D). | SHARE OF EACH DISCOM TO BE DISTRIBUTED ON PROPORTION TO THEIR ACTIVE ENERGY DRAWAL OF C
1) | NDPL | (ACTIVE ENERGY DRAWL= |  |  |  | 29.0035 | % |  |  | 0.1873 |  |  |  |  | -0.35271
2) | BRPL | (ACTIVE ENERGY DRAWL= |  |  |  | 39.7937 | % |  |  | 0.25699 |  |  |  |  | -0.48393
3) | BYPL | (ACTIVE ENERGY DRAWL= |  |  |  | 24.0691 | % |  |  | 0.15544 |  |  |  |  | -0.2927
4) | NDMC | (ACTIVE ENERGY DRAWL= |  |  |  | 6.3238 | % |  |  | 0.040839 |  |  |  |  | -0.076904
5) | MES | (ACTIVE ENERGY DRAWL= |  |  |  | 0.81 | % |  |  | 0.005231 |  |  |  |  | -0.0098504
Note :Sharing taken from wk-52 abt bill 2010-11

## FINAL EX. SUMMARY
DELHI TRANSCO LIMITED
REACTIVE ENERGY RELEASE STATEMENT TO LICENSEES.
PERIOD 1st MARCH-2011 TO 31st MARCH-2011
FINAL EXECUTIVE SUMMERY
[6 empty] | Energy for above 103% |  | Energy for below 97%
1 | NET REACTIVE ENERGY TO N.D.P.L. |  |  |  | + | 1.6394 | + | 14.0762
2 | NET REACTIVE ENERGY TO BSES RAJDHANI PO.LTD. |  |  |  |  | -0.20469 | + | 32.9007
3 | NET REACTIVE ENERGY TO BSES YAMUNA PO.LTD. |  |  |  | + | 1.2158 | + | 13.7459
4 | NET REACTIVE ENERGY TO NDMC |  |  |  | + | 6.4481 | + | 9.2128
5 | NET REACTIVE ENERGY TO MES |  |  |  | + | 0.56224 | + | 0.769
ALL FIGURES IN Mus.
Note:-
+ve sign indicates reactive energy drawl from the grid/system
-ve sign indicates reactive energy injected to the grid/system

## PRAGATI
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/11 | INTIAL READING 01/03/11 | DIFF. | CONSP. | REACTIVE MUs
PRAGATI
| (220 KV) | (EXPORT)
1 | GT-I | 4902492 | ELSTER | kvarh (lag) | 1500 | 990490 | 990459 | 31 | 46500 | 0.0465 | 981729 | 981739 | -10 | -15000 | -0.015
2 | GT-II | 4902493 | ELSTER | kvarh (lag) | 1500 | 987177 | 987373 | -196 | -294000 | -0.294 | 987365 | 987403 | -38 | -57000 | -0.057
3 | STG-III | 4902494 | ELSTER | kvarh (lag) | 1500 | 950323 | 950342 | -19 | -28500 | -0.0285 | 971577 | 971577 | 0 | 0 | 0
[8 empty] | NET REACTIVE ENERGY |  | -0.276 |  |  | NET REACTIVE ENERGY |  | -0.072
I.P.STATION
| (33KV) | (EXPORT)
1 | IBT-I | 4902509 | ELSTER | kvarh (lag) | 5000 | 996987 | 997002 | -15 | -75000 | -0.075 | 37855 | 37952 | -97 | -485000 | -0.485 | CTR CHANGE FROM 2000/5 TO 2000/1
2 | IBT-2 | 4902510 | ELSTER | kvarh (lag) | 1000 | 999547 | 999628 | -81 | -81000 | -0.081 | 9006 | 9859 | -853 | -853000 | -0.853 | ROLL OVER
3 | IBT-3 | 4864947 | ELSTER | kvarh (lag) | 1000 | 980519 | 980725 | -206 | -206000 | -0.206 | 992508 | 992749 | -241 | -241000 | -0.241
[8 empty] | NET REACTIVE ENERGY |  | -0.362 |  |  | NET REACTIVE ENERGY |  | -1.579

## VDY. BHAWAN ASSESSMENT
REACTIVE ENERGY CONSUMPTION STATEMENT OF VIDYUT BHAWAN LODHI ROAD
[7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
MONTH | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING | INTIAL READING | DIFF. | CONSP. | REACTIVE MUs | FINAL READING | INTIAL READING | DIFF. | CONSP. | REACTIVE MUs
APRIL-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 27750 | 27741 | 9 | 1800 | 0.0018 | 81655 | 80888 | 767 | 153400 | 0.1534
MAY-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 27893 | 27750 | 143 | 28600 | 0.0286 | 85992 | 81655 | 4337 | 867400 | 0.8674
JUNE-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 27977 | 27893 | 84 | 16800 | 0.0168 | 90600 | 85992 | 4608 | 921600 | 0.9216
JULY-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 28007 | 27977 | 30 | 6000 | 0.006 | 96598 | 90600 | 5998 | 1199600 | 1.1996
AUGUST-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 28157 | 28007 | 150 | 30000 | 0.03 | 99377 | 96598 | 2779 | 555800 | 0.5558
SEPTEMBER-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 29176 | 28157 | 1019 | 203800 | 0.2038 | 100564 | 99377 | 1187 | 237400 | 0.2374
OCTOBER-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 29445 | 29176 | 269 | 53800 | 0.0538 | 100649 | 100564 | 85 | 17000 | 0.017
NOVEMBER-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 30737 | 29445 | 1292 | 258400 | 0.2584 | 100671 | 100649 | 22 | 4400 | 0.0044
DECEMBER-2010 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 30608 | 30737 | -129 | -25800 | -0.0258 | 100667 | 100671 | -4 | -800 | -0.0008
JANUARY-2011 | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 30935 | 30608 | 327 | 65400 | 0.0654 | 100689 | 100667 | 22 | 4400 | 0.0044
|  |  |  | TOTAL |  |  |  |  | 0.6388 | Mus |  |  |  | 3.9602 | Mus
ENERGY ACCOUNTED IN REACTIVE ENERGY BILL FROM APRIL-10 TO JANUARY-2011 | [8 empty] | 0.3194 | Mus |  |  |  | 1.9801 | Mus
ASSESSMENT OF ENERGY FOR THE PERIOD APRIL-10 TO JANUARY-2011 DUE TO CHANGE OF M.F. FROM 100 TO 200 | [8 empty] | 0.3194 | Mus |  |  |  | 1.9801 | Mus